## Sheet4
Power Supply Number
1 | QTLD610100 | QTLD610100 | QTL | 1 | 276 | 390 | 280 | 350 | 1998-04-10 | -360 | BA7
2 | QTLF610200 | QTLF610200 | QTL | 1 | 276 | 390 | 340 | 450 | 1998-04-10 | -320 | BA7
3 | QTLD610300 | QTLD610300 | QTL | 1 | 276 | 390 | 230 | 300 | 1998-04-10 | -280 | BA7
4 | QTLF610400 | QTLF610400 | QTL | 1 | 276 | 390 | 315 | 400 | 1998-04-10 | -240 | BA7
5 | QTLD610500 | QTLD610500 | QTL | 1 | 276 | 390 | 295 | 400 | 1998-04-10 | -200 | BA7
6 | QTLF610600 | QTLF610600 | QTL | 1 | 276 | 390 | 225 | 300 | 1998-04-10 | -170 | BA7

## Sheet1
CNGS (450 geV)
Date de la dernière mise à jour : 24/7/2003
Magnet | Converter | Magnet | Magnet | Number | R per | L per | Inom | I max | Precision | Location | P.C. | Cable | Irms DC | Cable | Cable | Load | Load | L di/dt | U Max | Converter |  | Origin | Source | Umax | Imax | I AC peak | Installed | Flat top | Dimensions | I AC
Name | name | Name | Type | of | Magnet | magnet | max | DCCT |  | in the | Loc. | total | (DCCT x | section | R | R | L | t=1.7s |  | type | Serial |  |  | Conv. | Conv. | for I max | Power | power | lxdxh | rms
(Installation) |  | (Optics) |  | Magnets | (20º C) |  |  |  | (+/-) | tunnel |  | length | 0.55) | [7 empty] | Number |  |  |  |  | Converter | kVA | RxIn^2 |  | 0.55
|  |  |  | in Series | [mW] | [mH] | [A] | [A] |  | [m] |  | M |  | mm2 | mW | mW | mH | V | V | [6 empty] | (or DCCT) | peak | kW
MBSG410010 | MBSG 4100M | MBS | MBS | 8 | 6 | 7.5 | 3810 | 4400 | 1*10-4 | 125 | BB4 | 550 | 2420 | 2000 | 4.8125 | 58.0938 | 60 | 155.2941 | 410.9066 | R121* |  | SPS | 18000 | 510 | 6000 | 130.1194 | 4056.7202 | 843.2947 | 3.98x2.25xh | 71.5656
MBG 410147 | MBG 4101M | B1 | MBG | 73 | 4.88 | 5.7 | 5100 | 5400 | 5*10-5 | 190 | BA4 | 800 | 2970 | 1500 | 9.3333 | 402.1307 | 416.1 | 1321.7294 | 3493.235 | 2xRA3/T | 01 + 02 | LEP | 2x18kV | 3600 | 5400 | 811.512 | 25300.4403 | 10459.4186 |  | 446.3316
MDSV 412153 | MDSV 4121 | MDV1 | MDSV | 1 | 150 | 109 | 315 | 400 | 1*10-4 | 780 | BB4 | 1860 | 220 | 240 | 135.625 | 314.1875 | 109 | 25.6471 | 151.3221 | R33S |  | SPS | 400 | 262 | ± 400 | 215.3518 | 149.2001 | 31.1753 | 2.21x1.64x2.65 | 118.4435
MDSH 412243 | MDSH 4122 | MDH1 | MDSH | 1 | 150 | 109 | 315 | 400 | 1*10-4 | 810 | BB4 | 1920 | 220 | 240 | 140 | 319 | 109 | 25.6471 | 153.2471 | R33S |  | SPS | 400 | 262 | ± 400 | 215.3518 | 149.2001 | 31.6528 | 2.21x1.64x2.65 | 118.4435
MDSV 412419 | MDSV 4124 | MDV2 | MDSV | 1 | 150 | 109 | 315 | 400 | 1*10-4 | 830 | BB4 | 1960 | 220 | 240 | 142.9167 | 322.2083 | 109 | 25.6471 | 154.5304 | R33S |  | SPS | 400 | 262 | ± 400 | 215.3518 | 149.2001 | 31.9711 | 2.21x1.64x2.65 | 118.4435
MDSH 412421 | MDSH 4124 | MDH2 | MDSH | 1 | 150 | 109 | 315 | 400 | 1*10-4 | 830 | BB4 | 1960 | 220 | 240 | 142.9167 | 322.2083 | 109 | 25.6471 | 154.5304 | R33S |  | SPS | 400 | 262 | ± 400 | 215.3518 | 149.2001 | 31.9711 | 2.21x1.64x2.65 | 118.4435
QTLD 410100 | QTLD 4101 | QTL5 | QTL | 1 | 276 | 390 | 280 | 400 | 1*10-4 | 155 | BB4 | 610 | 220 | 240 | 44.4792 | 352.5271 | 390 | 91.7647 | 232.7755 | RB10 |  | LEP | 400 | 250 | 360 | 205.8897 | 142.6446 | 27.6381 | 3x.9x2 | 113.2393
QTGF 410200 | QTGF 4102 | QTN1 | QTG | 1 | 56 | 36 | 420 | 500 | 1*10-4 | 200 | BB4 | 700 | 275 | 240 | 51.0417 | 117.7458 | 36 | 10.5882 | 69.4612 | RB5 | 1 | LEP | 400 | 225 | 600 | 279.2653 | 193.4806 | 20.7704 | 3.6x.9x2.2 | 153.5959
QTGD 410300 | QTGD 4103M | QTND | QTG | 7 | 56 | 36 | 400 | 500 | 1*10-4 | 230 | BB4 | 760 | 275 | 240 | 55.4167 | 492.1583 | 252 | 74.1176 | 320.1968 | RB7 | 1 | LEP | 400 | 350 | 600 | 427.1116 | 295.9116 | 78.7453 | 3.6x.9x2.2 | 234.9114
QTGF 410400 | QTGF 4104M | QTNF | QTG | 7 | 56 | 36 | 380 | 500 | 1*10-4 | 260 | BB4 | 820 | 275 | 240 | 59.7917 | 496.9708 | 252 | 74.1176 | 322.6031 | RB7 | 3 | LEP | 400 | 350 | 600 | 427.1116 | 295.9116 | 71.7626 | 3.6x.9x2.2 | 234.9114
QTGD 411700 | QTGD 4117 | QTN5 | QTG | 1 | 56 | 36 | 380 | 500 | 1*10-4 | 660 | BB4 | 1620 | 275 | 240 | 118.125 | 191.5375 | 36 | 10.5882 | 106.357 | RB8 | 2 | LEP | 400 | 210 | 720 | 313.8284 | 217.4267 | 27.658 | 3.6x.9x2.2 | 172.6056
QTGF 411800 | QTGF 4118 | QTN6 | QTG | 1 | 56 | 36 | 430 | 500 | 1*10-4 | 685 | BB4 | 1670 | 275 | 240 | 121.7708 | 195.5479 | 36 | 10.5882 | 108.3622 | RB8 | 3 | LEP | 400 | 210 | 720 | 313.8284 | 217.4267 | 36.1568 | 3.6x.9x2.2 | 172.6056
QTGD 411900 | QTGD 4119 | QTN7 | QTG | 1 | 56 | 36 | 420 | 500 | 1*10-4 | 710 | BB4 | 1720 | 275 | 240 | 125.4167 | 199.5583 | 36 | 10.5882 | 110.3674 | RB8 | 4 | LEP | 400 | 210 | 720 | 313.8284 | 217.4267 | 35.2021 | 3.6x.9x2.2 | 172.6056
QTGF 412000 | QTGF 4120 | QTN8 | QTG | 1 | 56 | 36 | 260 | 500 | 1*10-4 | 735 | BB4 | 1770 | 275 | 240 | 129.0625 | 203.5687 | 36 | 10.5882 | 112.3726 | RB7 | 2 | LEP | 400 | 350 | 600 | 427.1116 | 295.9116 | 13.7612 | 3.6x.9x2.2 | 234.9114
QTGD 412100 | QTGD 4121 | QTN9 | QTG | 1 | 56 | 36 | 170 | 300 | 1*10-4 | 760 | BB4 | 1820 | 165 | 240 | 132.7083 | 207.5792 | 36 | 6.3529 | 68.6267 | RB2 | 18 | LEP | 400 | 200 | 300 | 124.848 | 86.4972 | 5.999 | 2.8x.9x2.2 | 68.6664
QTS 412200 | QTS 4122M | QTS10 | QTS | 1 | 120 | 198 | 270 | 400 | 1*10-4 | 790 | BB4 | 1880 | 220 | 240 | 137.0833 | 586.3917 | 588 | 138.3529 | 372.9096 | RB12 | 1 | LEP | 400 | 400 | 360 | 324.1667 | 224.5893 | 42.748 | 3x.9x2 | 178.2917
QTL 412204 |  | QTL10 | QTL | 1 | 276 | 390
QTL 412300 | QTL 4123M | QTL11 | QTL | 3 | 276 | 390 | 280 | 400 | 1*10-4 | 810 | BB4 | 1920 | 220 | 240 | 140 | 1064.8 | 1170 | 275.2941 | 701.2141 | RB9/O | 1 | LEP | 400 | 700 | 360 | 560.7208 | 388.4788 | 83.4803 | 3.6x.9x2.2 | 308.3965
QTS 412400 | QTS 4124M | QTS12 | QTS | 1 | 120 | 198 | 420 | 500 | 1*10-4 | 820 | BB4 | 1940 | 275 | 240 | 141.4583 | 894.8042 | 978 | 287.6471 | 735.0491 | R34XS |  | SPS | 400 | 710 | 500 | 710.7575 | 492.4272 | 157.8435 | 2.2x1.64x2.2 | 390.9166
QTL 412404 |  | QTL12 | QTL | 2 | 276 | 390
| SPBB4-R34XS | [6 empty] | 3/4/500 |  |  | BB4 | [8 empty] | R34XS |  | SPS | 400V | 710 | ± 500 |  |  | 0 | 2.2x1.64x2.2
| SPBB4-RB9/O | [6 empty] | 3/4/500 |  |  | BB4 | [8 empty] | RB9/O | 11 | LEP | 400V | 350 | 720 |  |  | 0 | 3.6x.9x2.2
1571.8303
[25 empty] | BB4 18 kV en kVA |  | 4056.7202
[25 empty] | BB4 400V en kVA |  | 3664.9332
Les convertisseurs MB alimentés depuis BA4 ne sont pas pris en compte